## Reservoir
Exhibit "D"
Common Facilities Storage Calculations
Development Name:
Tract Number:
Development (Excluding RV Parks) Usable Storage Requirement | [10 empty] | Development | Development | Storage | 2 |  | / gal
|  |  |  | Average |  |  | Max Day | Average | Max |  | Average | Max | Requirement | Cost |  |  | Cost
|  |  |  | Day Demand |  |  | Peaking | Day Demand | Day Demand | Number | Day Demand | Day Demand | Per | Per |  |  | For
|  |  |  | (gpd) |  | Capita/DU | Factor | (ADD) | (MDD) | Of Units | (ADD) | (MDD) | Unit | Unit |  |  | Development
Active Adult |  |  |  | 110 |  | 1.9 | 1.8 | 209 | 376 |  | 0 | 0 | 0 | 0 | 0 |  | 0
Single Family |  |  |  | 150 |  | 2.5 | 1.8 | 375 | 675 |  | 0 | 0 | 0 | 0 | 0 |  | 0
Single Family Manufactured / Mobile |  |  |  | 110 |  | 2.3 | 1.8 | 253 | 455 |  | 0 | 0 | 0 | 0 | 0 |  | 0
Multi-Family |  |  |  | 121 |  | 2 | 1.8 | 242 | 436 |  | 0 | 0 | 0 | 0 | 0 |  | 0
Commercial |  |  |  | 1700 | gpd/acre |  | 1.8 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
Developed Open Space |  |  |  | 1700 | gpd/acre |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 |  |  | 0
[9 empty] | 10% adjustment for line loses |  | 0 | 0
[9 empty] | Adjusted Totals |  | 0 | 0 |  | MDD gallon + line losses |  |  | #DIV/0!
Total
ADD | 0 |  |  |  | Storage
MDD | 0 |  |  |  | Capacity
Requirement
Stand By Storage ADD x |  | 2 |  |  | 0
Operational Storage ADD x |  | 15% |  |  | 0
Equalization Storage MDD x |  | 30% |  |  | 0
Fire Flow (Per Fire Dept.)
| Residential |  | x | 120 x 25% = | 0
| Commercial |  | x | 120 x 25% = | 0
0
Fire Flow requirement is 1,000 for residential development
and 1,500 if any commercial located within the development
Use only one (1)
RV Parks Usable Storage Requirement | [10 empty] | Development | Development | Storage | 2 |  | / gal
|  |  |  | Average |  |  | Max Day | Average | Max |  | Average | Max | Requirement | Cost |  |  | Cost
|  |  |  | Day Demand |  |  | Peaking | Day Demand | Day Demand | Number | Day Demand | Day Demand | Per | Per |  |  | For
|  |  |  | (gpd) |  | Capita/DU | Factor | (ADD) | (MDD) | Of Units | (ADD) | (MDD) | Unit | Unit |  |  | Development
RV Parks |  |  |  | 85 | per space | 1.9 | 1.8 | 161.5 | 291 |  | 0 | 0 | 0 | 0 | 0 |  | 0
[9 empty] | 10% adjustment for line loses |  | 0 | 0
[5 empty] | Total |  |  |  | Adjusted Totals |  | 0 | 0 |  | MDD gallon + line losses |  |  | #DIV/0!
ADD | 0 |  |  |  | Storage
MDD | 0 |  |  |  | Capacity
Requirement
Stand By Storage ADD x |  | 2 |  |  | 0
Operational Storage ADD x |  | 15% |  |  | 0
Equalization Storage MDD x |  | 30% |  |  | 0
Fire Flow (Per Fire Dept.)
| Residential |  | x | 120 x 25% = | 0 |  |  |  | The only inputs for Exhibits "D", "E", "F", and "G" are located on this page.
| Commercial |  | x | 120 x 25% = | 0 |  |  |  | Please fill in the applicable blue shaded areas. Put in the number of units for
the various residential types or RV Park spaces as well the acreage of commercial
Fire Flow requirement is 1,000 for residential development |  |  |  |  | 0 |  |  |  | Property.
and 1,500 if any commercial located within the development
Use only one (1) | [8 empty] | Next fill in the amount of "Fire Flow" required for residential / commercial
development. If a project contains both a residential and commercial component
Total Usable Storage Requirement | [8 empty] | just use the commercial requirement and leave the residential requirement blank.
Stand By Storage |  |  |  |  | 0 |  |  |  | At the top of the page input the Development or Project name and tract number.
Operational Storage |  |  |  |  | 0
Equalization Storage |  |  |  |  | 0
Fire Flow (Per Fire Dept.)
| Residential |  |  |  | 0
| Commercial |  |  |  | 0
0
* The minimum size storage tank is 500,000, however in the rare case where a smaller tank may be needed
the Operational Storage must be increased.

## Well
Exhibit "E"
Common Facilities Well Calculations
Development Name: | 0
Tract Number: | 0
[15 empty] | GPM Well | Well Cost
Development (Excluding RV Parks) Usable Storage Requirement | [9 empty] | Development | Development |  |  |  | 1000 | 2500000
|  |  | Average |  |  | Max Day | Average | Max |  | Average | Max |  |  |  | Percent | Cost |  | Cost
|  |  | Day Demand |  |  | Peaking | Day Demand | Day Demand | Number | Day Demand | Day Demand | Well |  |  | Of | Per |  | For
Category |  |  | (gpd) |  | Capita/DU | Factor | (ADD) | (MDD) | Of Units | (ADD) | (MDD) | Requirement |  | MDD GPM | GPM Well | Unit |  | Development
Active Adult |  |  | 110 |  | 1.9 | 1.8 | 209 | 376 | 0 | 0 | 0 | 0 | gpm | 0.38296 | 0.00038296 | 0 | 0 | 0
Single Family |  |  | 150 |  | 2.5 | 1.8 | 375 | 675 | 0 | 0 | 0 | 0 | gpm | 0.6875 | 0.0006875 | 0 | 0 | 0
Single Family Manufactured / Mobile |  |  | 110 |  | 2.3 | 1.8 | 253 | 455 | 0 | 0 | 0 | 0 | gpm | 0.46343 | 0.00046343 | 0 | 0 | 0
Multi-Family |  |  | 121 |  | 2 | 1.8 | 242 | 436 | 0 | 0 | 0 | 0 | gpm | 0.44407 | 0.00044407 | 0 | 0 | 0
Commercial |  |  | 1700 | gpd/acrd |  | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | gpm | 0 | 0 | 0 | 0 | 0
Developed Open Space |  |  | 1700 | gpd/acre |  |  | 0 | 0 | 0 | 0 | 0 | 0 | gpm | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | gpm | 1.978 | 0.001978 | 0 |  | 0
[8 empty] | 10% adjustment for line loses |  | 0 | 0 | 0 | gpm
[8 empty] | Adjusted Totals |  | 0 | 0 | 0 | gpm
[15 empty] | GPM Well | Well Cost
RV Parks Usable Storage Requirement | [9 empty] | Development | Development |  |  |  | 1000 | 2500000
|  |  | Average |  |  | Max Day | Average | Max |  | Average | Max |  |  |  | Percent | Cost |  | Cost
|  |  | Day Demand |  |  | Peaking | Day Demand | Day Demand | Number | Day Demand | Day Demand | Well |  |  | Of A 1,000 | Per |  | For
|  |  | (gpd) |  | Capita/DU | Factor | (ADD) | (MDD) | Of Units | (ADD) | (MDD) | Requirement |  | MDD GPM | GPM Well | Unit |  | Development
Category
RV Parks |  |  | 85 | per space | 1.9 | 1.8 | 161.5 | 290.7 | 0 | 0 | 0 | 0 | gpm | 0.29608 | 0.00029608 | 0 | 0 | 0
[8 empty] | 10% adjustment for line loses |  | 0 | 0 | 0 | gpm
[8 empty] | Adjusted Totals |  | 0 | 0 | 0 | gpm
[11 empty] | Total well requirement | 0 | gpm
Total well requirement is the total of all catagories times Max Day Demand divided by 18 hours / day divided by 60 minutes / hour

## Collections
Exhibit "F"
Common Facilities Collection Calculations
Development Name: | 0
Tract Number: | 0
Development (Excluding RV Parks) Usable Storage Requirement |  |  |  |  | Peak Hour |  |  |  | Development | Development
|  | Average |  |  | Flow | Average | Peak Hour |  | Average | Peak Hour | ADD |  | PF
|  | Day Demand |  |  | (PF) | Day Demand | Flow | Number | Day Demand | Flow | Collections |  | Collections
Category |  | (gpd) |  | Capita/DU | Factor | (ADD) | (PF) | Of Units | (ADD) | (PF) | Requirement |  | Requirement
Active Adult |  |  |  |  | 3 | 190 | 570 | 0 | 0 | 0 | 0 | gpm | 0 | gpm
Single Family |  |  |  |  | 3 | 240 | 675 | 0 | 0 | 0 | 0 | gpm | 0 | gpm
Single Family Manufactured / Mobile |  |  |  |  | 3 | 240 | 455 | 0 | 0 | 0 | 0 | gpm | 0 | gpm
Multi-Family |  |  |  |  | 3 | 180 | 436 | 0 | 0 | 0 | 0 | gpm | 0 | gpm
Commercial |  |  | gpd/acrd |  | 3 | 1500 | 0 | 0 | 0 | 0 | 0 | gpm | 0 | gpm
Developed Open Space |  |  | gpd/acre |  |  | 0 | 0 | 0 | 0 | 0 | 0 | gpm | 0 | gpm
[9 empty] | 0 | 0 | 0 | gpm | 0 | gpm
[7 empty] | 10% adjustment for line loses |  |  |  | 0 | gpm | 0 | gpm
[7 empty] | Adjusted Totals |  |  |  | 0 | gpm | 0 | gpm
RV Parks Usable Storage Requirement | [8 empty] | Development | Development
|  | Average |  |  | Peak Hour | Average |  |  | Average | Peak Hour | ADD |  | PF
|  | Day Demand |  |  | Flow | Day Demand |  | Number | Day Demand | Flow | Collections |  | Collections
|  | (gpd) |  | Capita/DU | (PF) | (ADD) |  | Of Units | (ADD) | (PF) | Requirement |  | Requirement
Category
RV Parks |  | 100 | per space |  | 3 | 100 | 300 | 0 | 0 | 0 | 0 | gpm | 0 | gpm
[7 empty] | 10% adjustment for line loses |  | 0 | 0 | 0 | gpm | 0 | gpm
[7 empty] | Adjusted Totals |  | 0 | 0 | 0 | gpm | 0 | gpm
[10 empty] | Total collections requirement | 0 | gpm | 0 | gpm

## WW Treatment
Exhibit "G"
Common Facilities Wastewater Treatment Calculations
Development Name: | 0
Tract Number: | 0
[13 empty] | Treatment |  | Treatment
Development (Excluding RV Parks) Usable Storage Requirement |  |  |  |  | Peak Hour |  |  |  |  | Development | Development |  | 2000000 | Cost | 15100000
|  | Average |  |  | Flow | Average | Peak Hour |  |  | Average | Peak Hour |  | Percent | Per Unit | Cost
|  | Day Demand |  |  | (PF) | Day Demand | Flow | Number |  | Day Demand | Flow | Treatment | Of | For | For
Category |  | (gpd) |  | Capita/DU | Factor | (ADD) | (PF) | Of Units |  | (ADD) | (PF) | Requirement | Treatment Expansion | Development | Development
Active Adult |  |  |  |  | 3 | 190 | 570 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Single Family |  |  |  |  | 3 | 240 | 675 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Single Family Manufactured / Mobile |  |  |  |  | 3 | 240 | 455 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Multi-Family |  |  |  |  | 3 | 180 | 436 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commercial |  |  | gpd/acrd |  | 3 | 1500 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Developed Open Space |  |  | gpd/acre |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% adjustment for line loses |  |  | 0 | 0 | 0
[7 empty] | Adjusted Totals |  |  | 0 | 0 | 0 |  | Cost per gallon of PF | #DIV/0!
[13 empty] | Treatment |  | Treatment
RV Parks Usable Storage Requirement | [9 empty] | Development | Development |  | 2000000 | Cost | 15100000
|  | Average |  |  | Peak Hour | Average |  |  |  | Average | Peak Hour |  | Percent | Per Unit | Cost
|  | Day Demand |  |  | Flow | Day Demand |  | Number |  | Day Demand | Flow | Treatment | Of | For | Per
|  | (gpd) |  | Capita/DU | (PF) | (ADD) |  | Of Units |  | (ADD) | (PF) | Requirement | Treatment Expansion | Development | Unit
Category
RV Parks |  | 100 | per space |  | 3 | 100 | 300 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 10% adjustment for line loses |  |  | 0 | 0 | 0
[7 empty] | Adjusted Totals |  |  | 0 | 0 | 0 |  | Cost per gallon of PF | #DIV/0!
[9 empty] | Total wastewater treatment requirement |  |  | 0